DOUBLE DISC CHECK VALVES

PART 1 – GENERAL

  - SECTION COVERS

- The design, manufacture, and testing of 2” through 24” double door check valves for the purpose of preventing reverse flow and minimizing valve slam in water applications.

  - REFERENCES & STANDARDS

- AWWA C518 “Double Disc Check Valves for Waterworks Service”

- ASTM A536 "Standard Specification for Ductile Iron Castings"

- ANSI B16.1 "Pipe Flanges and Flanged Fittings"

  - QUALITY ASSURANCE

- Valves shall be warranted by the manufacturer for defects in materials and workmanship for a period of one year (12 months) from date of shipment.

- Each valve shall be assembled, adjusted and tested as a unit by the valve manufacturer.

PART 2 – PRODUCTS

2.01      ACCEPTABLE MANUFACTURERS

- McWane Plant & Industrial (MPI)

- Kennedy Valve

- Clow Valve

- M&H Valve Company

  - DOUBLE DISC CHECK VALVES

- Valve body shall be wafer style of ductile iron construction per ASTM A536 and incorporate a vulcanized resilient EPDM seal.

- Discs shall be ASTM A351 – CF8M stainless steel and pivot about a T316 stainless steel hinge pin.

- Disc closure shall be assisted by a T316 stainless steel torsion spring.

- A T316 stainless steel stop pin shall be provided to stabilize disc movement in the full open position.

- Hinge and stops pins shall be stabilized by the inclusion of EPDM stabilization spheres to prevent wear from vibration during operation.

- Valves 10” and larger shall be provided with an eyebolt for lifting.

- Pressure rating shall be 250 psi. Valves shall be hydrostatically shell tested to 2 times the rated pressure per AWWA C518.

- The interior and exterior of the valve shall be coated with an NSF-61 approved fusion bonded epoxy coating.

PART 3 – INSTALLATION

- A minimum of 5 pipe diameters of straight pipe are recommended upstream of the check to ensure proper operation.

- When installed in a horizontal pipeline, it is recommended that the valve be installed with a vertically orientated hinge pin.