RESILIENT HINGE CHECK VALVES

PART 1 – GENERAL

  - SECTION COVERS

- The design, manufacture, and testing of 3” through 36” Ken-Flex check valves of the resilient hinge design for the purpose of preventing reverse flow and minimizing valve slam in water applications.

  - REFERENCES & STANDARDS

- AWWA C508 “Swing Check Valves for Waterworks Service”

- ASTM A536 "Standard Specification for Ductile Iron Castings"

- ANSI B16.1 "Pipe Flanges and Flanged Fittings"

  - QUALITY ASSURANCE

- Valves shall be warranted by the manufacturer for defects in materials and workmanship for a period of one year (12 months) from date of shipment.

- Each valve shall be assembled and tested by the valve manufacturer.

PART 2. PRODUCTS

2.01 ACCEPTABLE MANUFACTURERS

- McWane Plant & Industrial (MPI)

- Kennedy Valve

  - KEN-FLEX CHECK VALVES

- The valve body shall be ductile iron (ASTM A536 Grade 65-45-12) and allow full flow equal to nominal pipe diameter at all points through the valve. The seating surface shall be on a 45-degree angle to minimize disc travel. A threaded port with pipe plug shall be provided on the bottom of the valve to allow for field installation of a stainless-steel jackscrew device without special tools or removing the valve from the line.

- The valve cover shall be ductile iron (ASTM A536 Grade 65-45-12). An O-ring shall be provided in a machined groove in the valve body to provide a seal between the body and cover. A threaded port with pipe plug shall be provided in the access cover to allow for field installation of a stainless-steel disc position indicator.

- The disc shall be of one-piece construction, fully encapsulated with EPDM and molded with an integral O-ring seal.

- The valve disc shall be cycle tested 1,000,000 times in accordance with ANSI/AWWA C508 in both directions, and show no signs of wear, cracking or distortion.

- Valve shall be rated for 250psi working pressure. Valves shall be hydrostatically shell tested to 2 times the rated pressure per AWWA C508.

- The interior and exterior of the valve shall be coated with an NSF-61 approved fusion bonded epoxy.

PART 3 – INSTALLATION

- A minimum of 5 pipe diameters of straight pipe are recommended upstream of the check to ensure proper operation.