GATE VALVES

PART 1 – GENERAL

  - SECTION COVERS

- The design, manufacture, and testing of 3” through 48” gate valves of the metal seated design, for the purpose of providing isolation as indicated.

  - REFERENCES & STANDARDS

- AWWA C500 “Metal-Seated Gate Valves for Water Supply Service”

- ASTM A536 "Standard Specification for Ductile Iron Castings"

- ANSI B16.1 "Pipe Flanges and Flanged Fittings"

- AWWA C111 “Rubber-Gasketed Joints for Ductile-Iron Pressure Pipe and Fittings”

- NSF 61/372 “Drinking Water System Components – Health Effects”

  - QUALITY ASSURANCE

- Valves shall be warranted by the manufacturer for defects in materials and workmanship for a period of one year (12 months) from date of shipment.

- Each valve and actuator shall be assembled, adjusted and tested as a unit by the valve manufacturer.

PART 2 – PRODUCTS

2.01      ACCEPTABLE MANUFACTURERS

- McWane Plant & Industrial (MPI)

- M&H Valve Company

- Kennedy Valve

- Clow Valve

  - ROTATING DISC GATE VALVES

- Valve body and bonnet shall be ductile iron per ASTM A536.

- Valve wedge shall be a single piece cast of ductile iron per ASTM A536. Wedge shall be free of any pockets, linkages, or pins.

- Valve disc and body seat rings shall be bronze.

- Valve stems shall be stainless steel with integral collar in full compliance with AWWA.

- Valve shall be either non-rising stem (NRS) or rising stem (OS&Y), open by turning left or right, and provided with a 2” operating nut or handwheel.

- NRS valves shall be provided with conventional packing or double O-rings. OS&Y valves shall be provided with conventional packing. Stem packing shall be field replaceable, such that the valve can be packed under pressure when in the fully open position.

- When specified, valves 14” and larger installed in a horizontal orientation shall be provided with a roller, track, and scraper system.  The roller, track, and scraper system shall consist of a bronze scraper and two bronze rollers affixed to a modified wedge which travel along a bronze body guide to remove sediment buildup during operation.

- When specified, valves 14” and larger installed in a vertical orientation shall be provided with two integrally cast flushing ports. Drain plugs used as flushing ports will not be accepted.

- When specified, valves 16” and larger shall be provided with a bypass valve. Bypass type and materials provided as specified.

- Pressure ratings shall be 250 psi for class 125 valves and 300 psi for class 250. Valves shall be hydrostatically shell tested to 2 times the rated pressure per AWWA C500.

- Valves 14” and larger shall be provided with a bevel gear for horizontal valve orientations or spur gear for vertical orientations.

- All valve fasteners shall be stainless steel.

- The interior and exterior of the valve shall be coated with an NSF-61 approved two-part epoxy.

- Each valve shall have manufacturer’s name, pressure rating, and year in which it was manufactured cast in the body.

PART 3 – INSTALLATION

- Vertical installation orientations are preferred whenever possible, allowing gravity to assist with valve closure, resulting in lower operating torque requirements.